SPECIFICATIONS

PVC Insulated PVC Sheathed Flat steel Armoured Aluminum L.T Under Ground Power cable, 1100 V Grade confirming to IS 1554 Part -1 with latest amendments: Type Code: AYFY

Conductor Material

Aluminium as per Class-2 of IS: 8130, Stranded Compacted Shaped

Insulation Material :

PVC Type-C as per IS: 5831, Colour : Red, Yellow, Blue & Black

Inner Sheath : PVC Type ST-2 as per IS: 5831

Outer Sheath : PVC Type ST-2 as per IS: 5831

Armouring :

Single Layer of Galvanized Steel Flat Strip

Sizes & Quantities:

- 4C  x  16  Sq.mm ----     1000 Mtrs.

2.   3.5 C x 25 Sq.mm ----   1000 Mtrs.

3.   3.5 C x 35 Sq.mm ----   1000 Mtrs.

4.   3.5 C x 50 Sq.mm ----   1000 Mtrs

5.   3.5C x 70 Sq.mm ----    1000 Mtrs.

6.   3.5 C x 95 Sq.mm ----   1000 Mtrs.

7    3.5C x 120 Sq.mm ---   1000 Mtr

8.   3.5C x 150 Sq.mm ---   1000 Mtr

9.   3.5C x 185 Sq.mm ---   1000 Mtr

10. 3.5C x 240 Sq.mm ---   1000 Mtr

11. 3.5C x 300 Sq.mm ---   1000 Mtr

Make:

CCI/Incab/Universal/RPG/Nicco/Torrent/Polycab/Paramount/KEI/Havells/

Finolex/Gloster/V-Guard/L&T/Primecab/RR Kabel/Auracab

The following details shall be marked sequentially for each meter run length of the cable by non-erasable embossing on the outer sheath:

Reference to Indian Standard

Name of the manufacturer/Trade Name

Configuration of the cable: viz. Voltage grade, no. of core, sq.mm, AYFY

Year of manufacturing

Sequential marking of running meter length of the cable shall be identified at regular intervals of one meter.

Each drum shall consist of single length cable of 500 metres.

The cable shall be placed on drums in such a manner that it will be protected from injury during transit.  Each end of the cable shall be firmly and properly secured to the drum. No undue stress shall appear on cables when laid on drums.

The cable drum shall carry the following information:

Reference to the Indian Standard.

Manufacturer’s name, brand or trade mark

Type of cable and voltage grade.

No. of cores, Nominal cross-sectional area of conductor

Cable code

Length of cable on drum

All the routine tests as per IS shall be conducted and passed as per the limits given in the standards.  All the bought out certificates will be verified and the test results shall be as per respective standards.